## Sheet1
Item: Curtain
Reference: Ahonen, A., M. Kokkala and H. Weckman. Burning Characteristics of Potential Ignition Sources of Room Fires. Technical Research centre of Finland. Espoo, Finland. Research Report 285. June 1984.
Heat Release Rate History
Test 9 - Cotton Velvet (Serenadi/Seligren)
Test 10 - 45% PC / 16% PE / 39% CO (Regina II/Finlayson)
Test 11 - 45% PC / 16% PE / 39% CO (Regina II/Finlayson)
| Test 9 |  | Test 10 |  | Test 11
| Time (s) | HRR (kW) | Time (s) | HRR (kW) | Time (s) | HRR (kW)
| 132.3729 | 2.2428 | 341.3436 | 1.9633 | 471.6951 | 1.5927
| 144.5772 | 13.7348 | 351.3838 | 18.67 | 483.8994 | 13.0847
| 149.8803 | 63.3044 | 357.0483 | 48.4147 | 493.6828 | 43.8776
| 158.9408 | 133.7472 | 364.7818 | 78.1617 | 501.226 | 84.0589
| 166.132 | 193.2318 | 374.5938 | 107.3895 | 504.9929 | 104.4103
| 173.7799 | 227.6742 | 388.8289 | 120.9707 | 515.0236 | 121.6388
| 173.6087 | 237.065 | 394.9025 | 128.2819 | 523.033 | 136.2562
| 183.9152 | 239.1638 | 411.4443 | 128.8228 | 531.1564 | 144.6132
| 194.6118 | 219.8725 | 426.2788 | 109.5363 | 541.4535 | 147.2337
| 209.7031 | 186.4999 | 451.7907 | 72.002 | 554.1714 | 130.5534
| 246.1399 | 117.1533 | 477.0458 | 48.5538 | 569.3197 | 94.0505
| 265.4736 | 78.0466 | 527.128 | 25.1344 | 594.9553 | 49.734
| 288.8881 | 42.075 | 585.3146 | 11.1154 | 620.1534 | 29.416
| 311.9221 | 26.9718 | 635.0544 | 6.4776 | 653.5034 | 15.89
| 343.1461 | 16.5736 | 701.3264 | 2.9024 | 703.2907 | 8.6436
| 382.5983 | 8.7935 | 753.0495 | 2.9623 | 750.9615 | 4.0034
| 436.4664 | 4.6822 | 800.6537 | 1.9741 | 784.0833 | 2.9983
| 488.2085 | 3.6987 |  |  | 815.1362 | 1.9909